Attachment 2

Explanatory Notes

Draft Queensland Development Code, Mandatory Part 1.4 – Building over or near relevant infrastructure (sewer, water main and stormwater drain)

Background

Sewers or water mains

Section 192 of the Water Supply (Safety and Reliability) Act 2008 (WS (S&R) Act) states that a person must not, without the written consent of a service provider, interfere with the service provider’s infrastructure.  This requirement is reflected in section 83 of the Building Act 1975 (BA) which provides that a private certifier must not grant a building development approval if the proposed building work is over or adjacent to a sewer or water main until consent under the WS (S&R) Act has been granted.

The WS (S&R) Act does not specify the criteria that must be addressed by a service provider, or the process to be followed, when making an application.  There are also no consistent mandatory design standards to provide information on whether it is appropriate to build over or adjacent to a service provider’s infrastructure.

Some Local Governments require a planning development application for building work over or near sewers and water mains, even though consent is required under the WS (S&R) Act.

There is no appeal process available for applicants dissatisfied with a decision made under s192 of the WS(S&R) Act.

Stormwater drains

Section 83 of the BA does not require consent for building work over or adjacent to a stormwater drain. Stormwater drains are administered under the Local Government Act 2009 and are owned by either a Local Government or a private lot owner.  There is no consistent process across the State about how this type of building work is regulated.

2011 consultation process

Building Newsflash number 480 was issued on 19 September 2011 and sought public comment on a proposal to mandate a revised version of the current Queensland Development Code Non-Mandatory Part (NMP) 1.4 – ‘Excavation and Piling near Sewers, Stormwater Drains and Water Mains’ (NMP 1.4). The revised part was titled MP 1.4 Building over or near sewer, stormwater and water mains (draft QDC). The draft QDC provided that building certifiers would oversee building work that complied with the acceptable solutions of the code and that concurrence advice from local governments or water service providers would be needed for building work that used a performance solution to comply.  The draft QDC provided that the Building and Development Dispute Resolution Committees (BDDRC) would hear appeals on these matters.

Following consultation, the Department of Housing and Public Works (DHPW) revised  the draft QDC.  It is proposed to adopt the revised draft QDC as a new QDC Mandatory Part 1.4 which will provide detailed criteria for building work over or near a service provider’s infrastructure. The draft QDC is now titled Mandatory Part 1.4 – Building over or near relevant infrastructure (sewer, water main and stormwater drains).

Policy objectives and the reasons for them

The purpose of the draft QDC is to provide a timely and consistent assessment of building work over or near relevant infrastructure across Queensland.  In addition, the proposed changes will provide for a simple and cost effective appeal process.

The current regulatory process for building over or near an infrastructure service is complex.  There are no timeframes or criteria for consent and approval mechanisms are not uniform across Queensland.  An application may require assessment against the BA, the WS (S&R) Act and a planning scheme.

Under the proposal, it is expected that there will be a reduction in red tape for applicants, as building work over or near an infrastructure service will only need to be assessed against a single standard under the QDC. The standard will apply across the State, which will provide certainty and consistency.

The proposed changes will clarify that building work over or near an infrastructure service is assessed under the BA as part of the building assessment provisions.  By virtue of section 78A of the Sustainable Planning Act 2009 (SPA) and section 31 of the BA, the provisions of the QDC will prevail over a local planning instrument that includes such provisions.

Local Governments (and other service providers or water entities) will have the ability, through the referral agency process to direct outcomes of applications for building work that do not comply with the acceptable solutions of the QDC.

The QDC will enable building work over or near existing relevant infrastructure to be carried out so that it does not damage a relevant service provider’s relevant infrastructure. It will also enable a relevant service provider to gain access to its relevant infrastructure to undertake ongoing inspection, maintenance and replacement work.

The BDDRC will have jurisdiction to hear appeals from decisions of a referral agency.

Achievement of policy objectives

The QDC provides performance requirements and acceptable solutions for the design and construction of all new building work over or near a relevant service provider’s infrastructure, and incorporates access provisions to enable a relevant service provider to carry out inspection, maintenance and replacement.

Application

A building certifier will assess a building development application against the QDC. It will no longer be necessary to obtain consent from a service provider for this part of the building construction (i.e. load bearing footings, suitable access to services for inspection or maintenance). If the application is consistent with the QDC, no further consents will be required.

Due to the fact that acceptable solutions will apply to the simpler classes of buildings such as houses, townhouses, duplexes sheds and structures (including decks, retaining walls and swimming pools) the relevant service provider will receive fewer applications for review.  This will result in cost efficiencies for relevant service providers as they will only have to approve the more complex applications as the concurrence agency.

Referral Agency

Class 1 buildings and Class 10 buildings or structures

If the application does not comply with the acceptable solutions in the draft QDC, a concurrence agency response will be triggered to consider an alternative solution. The Local Government, water entity or service provider will be the concurrence agency.

Note: Local Governments in south-east Queensland will be concurrence agencies until 2013 (unless otherwise extended by legislation), as these Local Governments are delegates for distributor-retailers for development applications.

It is proposed that the acceptable solutions of the QDC will only apply to building development applications for class 1 buildings (such as houses and townhouses) and class 10 buildings or structures (such as sheds and retaining walls).

Class 2 to 9 buildings

Referral to a concurrence agency will automatically occur for applications involving class 2-9 buildings.

As building development applications for class 2-9 buildings (such as units, offices, shops, warehouses etc.) are more complex, they will, in all cases, be referred to the relevant service provider as a concurrence agency under the Sustainable Planning Regulation 2009 (SPR).  Once referred by a building certifier, the concurrence agency will assess the application against the performance requirements of the QDC.

Other limitations

Acceptable solutions are further limited to building work where the service pipes are a particular size. For sewers and water mains, the size is 225mm nominal diameter or less, and for stormwater mains, 375mm nominal diameter or less. For larger pipes or pipes deeper than 1.5m, the application will be referred to the relevant agency for concurrence response.

If the relevant infrastructure is a pressure pipeline of any size then it will require concurrence agency response.

The proposed QDC will not apply where there is an easement for relevant infrastructure registered with the Queensland Titles Registry.  If building work for any class of building or a structure is being carried out within a registered easement then it must meet the easement requirements.

Note that it is possible for building designs intending construction over relevant infrastructure to meet the acceptable solutions in A1 (for structural stability). However, the building designs intended construction will also need to meet the acceptable solutions in A2 (access to the infrastructure). As A2 does not permit building over relevant infrastructure then a concurrence agency response will be required.  Thus, building designs intending construction over relevant infrastructure may satisfy A1 but not A2 (access to the infrastructure) of the proposed QDC.

An example of the above scenario would be locating a deck over a sewer main at the back of a lot.  The footings of the deck may be a sufficient distance away from the sewer to satisfy the structural stability requirements under A1, however, placing the deck over the sewer would impede access (not satisfying the acceptable solutions for access under A2).  For this reason, the building design would require concurrence agency response as to whether it meets performance requirement 2.

In all cases these type of building designs will require concurrence agency response.

Disputes/Appeals

The proposed use of the draft QDC for assessment of this building work, will mean the BDDRC has jurisdiction for hearing appeals under SPA.  The BDDRC will provide a quick and cost effective dispute resolution service for applicants dissatisfied with decisions made by a service provider, Local Government or building certifier.

- Appeals to the BDDRC are generally decided within 3-5 weeks by referees with appropriate expertise.

Notes on provisions

Purpose

The purpose of the draft QDC is to enable:

- building work over or near existing relevant infrastructure to be carried out so that it does not damage the relevant infrastructure; and

- a relevant service provider to gain access to relevant infrastructure to undertake ongoing inspection, maintenance and replacement.

Commencement

Subject to approval by Government, it is anticipated that the draft QDC will commence by mid-2013.

Application

The proposed draft QDC will apply to all building classes and structures on sites containing sewer or stormwater drainage lines or water mains (other than a lot owner’s sanitary drainage, water supply and stormwater drain pipes).

It should be noted that where an adjoining lot contains relevant infrastructure which may be adversely affected by building work on the applicant’s lot then P1 of the proposed QDC will apply.

The proposed draft QDC will not apply to an infrastructure service where there is an easement right registered with the Queensland Titles Registry relating to the infrastructure service.  Building work for a building of any class or structure that is located within a registered easement must meet the easement requirements.

Referral agency

Where an alternative solution is being used to meet the performance requirements of the QDC, a concurrence agency response will be triggered.  An alternative solution will be required where the acceptable solutions cannot be met in whole or part.

Compliance with the QDC

As with all assessable building work, compliance can be obtained in a number of ways, including by compliance with the relevant acceptable solution for the performance requirement, formulating an alternative solution that complies with the performance requirement or a combination of the two (refer section 14 of the BA).

Definitions

Some of the important definitions in the QDC are:

relevant infrastructure – means a sewer, water main and stormwater drain of a relevant service provider .

“Sewer”, “water main” and “stormwater drain” are also defined and include maintenance covers. .

zone of influence - of a building or structure means the area determined to be loaded by the footings or other load-bearing elements of the building or structure.

Note: The example in Figure 1 of the QDC does not state a value for the angle of repose. The value of the angle of repose is dependent on the soil type.

The significance of this definition is to specify the load zones for building work that have the potential to adversely impact on the relevant infrastructure.. For example, a value of 45º may cater for most cases and is the maximum angle extending upwards from the horizontal plane (the angle of repose) in which the load bearing elements of a building or structure may impact upon relevant infrastructure. While a 45º angle takes into account the typical cases for common soil types and volume, where cohesionless soil such as sand or gravel is present, an angle closer to 30º may be more appropriate.

Performance requirements (P) and Acceptable Solutions (A)

P1 and A1

P1 relates to the carrying out of building work over or near a relevant service provider’s infrastructure. P1 is designed to provide protection to relevant infrastructure from damage caused by the load transference of a building or structure.

Under A1(e), compliance can be achieved by ensuring the load zone (zone of influence) of the footings or other load-bearing elements of the building or structure remains away from the relevant infrastructure.

Alternatively, if the lot size, soil type or desired design do not allow a building or structure to be built applying the above solution (where infrastructure remains away from the load zone), then other acceptable solutions are provided. For example, the base of the footings of the building or structure can be extended at least 300mm below the invert level of the relevant infrastructure.  Where it is not possible to locate the building work so the relevant infrastructure is outside the zone of influence, another solution is to use screwed or bored piles or piers to support the footings of the building or structure not less than 1.2 m from the centreline of the pipe.  Using this approach, the zone of influence must still extend at least 300mm below the invert level of the relevant infrastructure.

If the applicant is unable to meet an acceptable solution then an alternative solution can be devised.

A1 also provides acceptable solutions for carrying out filling or excavation work to ensure that this type of work does not place any additional loading on, or reduce cover to relevant infrastructure..

Figure 4 provides an example to help clarify that when excavation work is carried out a minimum cover of 600mm must be maintained around the relevant infrastructure at all times. A1 also restricts the use of a vibrating roller within 2m (measured horizontally) of the centreline of the relevant infrastructure.

Fill associated with building work that is placed over relevant infrastructure must not result in a fill depth of more than 1m.

P2 and A2

P2 includes provisions to allow adequate access to the relevant infrastructure by the relevant service provider to enable ongoing inspection, maintenance and replacement. The acceptable solutions provide clearance distances (unobstructed vertical and horizontal) to enable access for work to be carried out on relevant infrastructure by the relevant service provider.

For example, A2(d) specifies that if a pipe does not exceed a depth of 1.5m then the unobstructed vertical distance required from the finished surface level is 2.4m. An alternative solution will be required where sewers, water mains and stormwater drains exceed a depth of 1.5m to the invert level of the pipe.

A2(e) also requires the proximity of gravity walls to relevant infrastructure to be considered.  Once a gravity wall exceeds 1m in height, a registered professional engineer must consider the design and its ability to provide safe access for ongoing maintenance of the infrastructure.

All clearance distances specified by A2 were developed to reflect current best practice for undertaking maintenance and repair on infrastructure services.  Industry feedback suggests that non-dig technology (electric eels, fibre optic cameras, water dyes) and/or a Bobcat or small/mini excavator which fit between typical residential side boundaries are commonly used and would operate within the specified distances.

A2(g) requires an unobstructed horizontal distance of 1.5m and an unobstructed vertical distance of 2.4m for all sewers, water mains and stormwater drains.  This solution ensures a clear area of appropriate height and width is provided in proximity to infrastructure to allow machinery to carry out work.

A2(h) further includes requirements for clear areas around infrastructure such as maintenance covers.  This ensures ready access is provided for these structures in the event maintenance or repair is required.  An unobstructed vertical distance of 2.4m is also prescribed for maintenance covers and jump-ups so that repairers have sufficient access for machines or other technology to carry out work.

nominal diameter means the outside diameter of a sewer, water main or stormwater drain, including its wall thickness.